## Sheet1
Attempt to model the performance of an MVHR evaporative cooler during a 24 hour period
Notes
Generally
The MVHR cooler is installed on the main MVHR extract, before the MVHR unit
The coolth from the cooler is transferred to the supply air via the MVHR heat exchanger
This spreadsheet may contain bugs & errors
The 'potential internal temperatures' have not been tested against real data
Data entry
Yellow cell background = data input cell
No cells are protected - take care
Data results
Blue text = calculated value
Red text = calculated value with warning
1 | Building volume
|  |  | Measured volume of the building | 125 | m³
|  |  | Fabric air leakage | 0.6 | ach
|  |  | Volume of building + air lost through leakage | 200 | m³
2 | MVHR speed settings
|  |  | Low fan speed air flow rate | 50 | m³/hr | 25% | of the building volume + fabric air loss volume
|  |  | Mid fan speed airflow rate | 100 | m³/hr | 50% | of the building volume + fabric air loss volume
|  |  | High (boost) fan speed airflow rate | 150 | m³/hr | 75% | of the building volume + fabric air loss volume
3 | Evaporative cooler details
|  |  | Manufacturer's maximum water flow rate | 5 | L/hr
|  |  | Manufacturer's humidity sensor cutout | 85% | RH | (for info & to verify the line below)
|  |  | Humidifying limit to used in these calculations (see note) | 80% | RH | OK
4 | Weather forecast for day to be modelled |  |  |  |  | Time of day | [23 empty] | Max | Notes & warnings
|  |  | Date being modelled | 2025-07-29 |  | 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
|  |  | Average temperature external |  | °C | 26 | 25 | 24 | 23 | 22 | 21 | 21 | 23 | 24 | 26 | 27 | 29 | 31 | 32 | 33 | 34 | 36 | 36 | 35 | 35 | 33 | 31 | 29 | 27 | 36
|  |  | Relative humidity external |  | % | 56% | 59% | 61% | 65% | 70% | 73% | 74% | 70% | 64% | 60% | 55% | 49% | 43% | 39% | 36% | 33% | 31% | 29% | 29% | 31% | 34% | 41% | 48% | 53% | 74% | OK
|  |  | Absolute humidity (water in air) at this °C & RH |  | g/m³ | 13.6387 | 13.5853 | 13.2736 | 13.3606 | 13.5853 | 13.3708 | 13.554 | 14.3883 | 13.9264 | 14.6129 | 14.1623 | 14.0858 | 13.7769 | 13.1835 | 12.8345 | 12.403 | 12.9342 | 12.0998 | 11.4863 | 12.2784 | 12.1215 | 13.1361 | 13.7984 | 13.6473 | 14.6129
|  |  | Air pressure (only used as a check; see important comment) |  | hPa | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | 1013 | OK
|  |  | Approximate wet bulb temp (see important comment) |  | °C | 19.7949 | 19.3559 | 18.7467 | 18.3957 | 18.1432 | 17.597 | 17.725 | 19.0748 | 19.171 | 20.4013 | 20.5211 | 21.2644 | 21.8512 | 21.869 | 22.0256 | 22.1201 | 23.1598 | 22.6337 | 21.8852 | 22.3983 | 21.576 | 21.4608 | 21.0902 | 20.203 | 23.1598
5 | Theoretical: water to evaporate to reach 100% RH
|  |  | Saturation vapor pressure @ wet bulb temperature |  | Pa | 2307.4031 | 2245.2823 | 2161.5132 | 2114.5033 | 2081.2479 | 2010.8567 | 2027.1587 | 2206.2849 | 2219.5689 | 2395.6938 | 2413.4949 | 2526.4698 | 2618.9266 | 2621.7703 | 2646.9656 | 2662.2574 | 2835.8282 | 2746.8025 | 2624.3651 | 2707.765 | 2575.2092 | 2557.0912 | 2499.5857 | 2366.5108 | 2835.8282
|  |  | Absolute humidity @ wet bulb temperature (100% RH) |  | g/m³ | 17.0669 | 16.6323 | 16.0452 | 15.7152 | 15.4814 | 14.9859 | 15.1007 | 16.3592 | 16.4523 | 17.6833 | 17.8075 | 18.594 | 19.2361 | 19.2558 | 19.4305 | 19.5365 | 20.7372 | 20.1219 | 19.2738 | 19.8518 | 18.9326 | 18.8068 | 18.407 | 17.4797 | 20.7372
|  |  | Water to evaporate to achieve 100% RH |  | g/m³ | 3.4281 | 3.047 | 2.7716 | 2.3546 | 1.8961 | 1.6151 | 1.5467 | 1.9709 | 2.5258 | 3.0704 | 3.6452 | 4.5081 | 5.4592 | 6.0723 | 6.596 | 7.1335 | 7.803 | 8.0222 | 7.7875 | 7.5734 | 6.8112 | 5.6707 | 4.6086 | 3.8325 | 8.0222
6 | Evaporative Cooler performance
|  |  | Approximate extract air temp after cooling (see note) |  | °C | 21.0359 | 20.4847 | 19.7974 | 19.3166 | 18.9146 | 18.2776 | 18.38 | 19.8598 | 20.1368 | 21.521 | 21.8169 | 22.8115 | 23.681 | 23.8952 | 24.2205 | 24.496 | 25.7278 | 25.307 | 24.5082 | 24.9186 | 23.8608 | 23.3686 | 22.6722 | 21.5624 | 25.7278
|  |  | Absolute humidity @ the cooler's humidifying limit | (80% RH) | g/m³ | 13.6535 | 13.3059 | 12.8362 | 12.5721 | 12.3851 | 11.9887 | 12.0806 | 13.0873 | 13.1618 | 14.1467 | 14.246 | 14.8752 | 15.3889 | 15.4046 | 15.5444 | 15.6292 | 16.5898 | 16.0976 | 15.419 | 15.8814 | 15.1461 | 15.0454 | 14.7256 | 13.9838 | 16.5898
|  |  | Water to add to achieve the cooler's humidifying limit |  | g/m³ | 0.014771 | -0.27942 | -0.43744 | -0.78844 | -1.2002 | -1.3821 | -1.4734 | -1.301 | -0.76461 | -0.46627 | 0.083715 | 0.78934 | 1.6119 | 2.2211 | 2.7099 | 3.2262 | 3.6556 | 3.9978 | 3.9328 | 3.603 | 3.0246 | 1.9093 | 0.92723 | 0.33652 | 3.9978
7 | MVHR supply air temperature
|  |  | Approx air supply temp (°C) based on coolth recovery rate of: | 92% | °C | 21.433 | 20.8459 | 20.1336 | 19.6112 | 19.1614 | 18.4954 | 18.5896 | 20.1111 | 20.4459 | 21.8793 | 22.2316 | 23.3066 | 24.2665 | 24.5436 | 24.9229 | 25.2564 | 26.5496 | 26.1624 | 25.3475 | 25.7251 | 24.592 | 23.9791 | 23.1784 | 21.9974 | 26.5496
|  |  | Approx air supply temp after a distribution loss of, say | 20% | °C | 22.3464 | 21.6767 | 20.9069 | 20.289 | 19.7291 | 18.9963 | 19.0717 | 20.6888 | 21.1567 | 22.7035 | 23.1852 | 24.4453 | 25.6132 | 26.0349 | 26.5383 | 27.0051 | 28.4397 | 28.1299 | 27.278 | 27.5801 | 26.2736 | 25.3833 | 24.3427 | 22.9979 | 28.4397
8 | Temperature of air within the building
MVHR low fan speed
|  |  | Water evaporated |  | L/h | 0.00073853 | -0.013971 | -0.021872 | -0.039422 | -0.060009 | -0.069106 | -0.07367 | -0.065048 | -0.038231 | -0.023313 | 0.0041857 | 0.039467 | 0.080597 | 0.11106 | 0.1355 | 0.16131 | 0.18278 | 0.19989 | 0.19664 | 0.18015 | 0.15123 | 0.095465 | 0.046362 | 0.016826 | 0.19989 | OK
|  |  | Potential building air temperature |  | °C | 25.0866 | 24.1692 | 23.2267 | 22.3222 | 21.4323 | 20.4991 | 20.5179 | 22.4222 | 23.2892 | 25.1759 | 26.0463 | 27.8613 | 29.6533 | 30.5087 | 31.3846 | 32.2513 | 34.1099 | 34.0325 | 33.0695 | 33.145 | 31.3184 | 29.5958 | 27.8357 | 25.9995 | 34.1099
|  |  | Potential temperature reduction (see warning below) |  | °C | -0.9134 | -0.83082 | -0.77329 | -0.67775 | -0.56771 | -0.50093 | -0.48209 | -0.57779 | -0.71082 | -0.82414 | -0.95369 | -1.1387 | -1.3467 | -1.4913 | -1.6154 | -1.7487 | -1.8901 | -1.9675 | -1.9305 | -1.855 | -1.6816 | -1.4042 | -1.1643 | -1.0005 | -1.9675
MVHR mid fan speed
|  |  | Water evaporated |  | L/h | 0.0014771 | -0.027942 | -0.043744 | -0.078844 | -0.12002 | -0.13821 | -0.14734 | -0.1301 | -0.076461 | -0.046627 | 0.0083715 | 0.078934 | 0.16119 | 0.22211 | 0.27099 | 0.32262 | 0.36556 | 0.39978 | 0.39328 | 0.3603 | 0.30246 | 0.19093 | 0.092723 | 0.033652 | 0.39978 | OK
|  |  | Potential building air temperature |  | °C | 24.1732 | 23.3384 | 22.4534 | 21.6445 | 20.8646 | 19.9981 | 20.0358 | 21.8444 | 22.5784 | 24.3517 | 25.0926 | 26.7226 | 28.3066 | 29.0174 | 29.7691 | 30.5025 | 32.2198 | 32.065 | 31.139 | 31.2901 | 29.6368 | 28.1917 | 26.6714 | 24.999 | 32.2198
|  |  | Potential temperature reduction (see warning below) |  | °C | -1.8268 | -1.6616 | -1.5466 | -1.3555 | -1.1354 | -1.0019 | -0.96417 | -1.1556 | -1.4216 | -1.6483 | -1.9074 | -2.2774 | -2.6934 | -2.9826 | -3.2309 | -3.4975 | -3.7802 | -3.935 | -3.861 | -3.7099 | -3.3632 | -2.8083 | -2.3286 | -2.001 | -3.935
MVHR high (boost) fan speed
|  |  | Water evaporated |  | L/h | 0.0022156 | -0.041913 | -0.065616 | -0.11827 | -0.18003 | -0.20732 | -0.22101 | -0.19514 | -0.11469 | -0.06994 | 0.012557 | 0.1184 | 0.24179 | 0.33317 | 0.40649 | 0.48393 | 0.54833 | 0.59967 | 0.58992 | 0.54045 | 0.4537 | 0.2864 | 0.13908 | 0.050479 | 0.59967 | OK
|  |  | Potential building air temperature |  | °C | 23.2598 | 22.5076 | 21.6801 | 20.9667 | 20.2969 | 19.4972 | 19.5537 | 21.2666 | 21.8675 | 23.5276 | 24.1389 | 25.5839 | 26.9599 | 27.5262 | 28.1537 | 28.7538 | 30.3298 | 30.0974 | 29.2085 | 29.4351 | 27.9552 | 26.7875 | 25.507 | 23.9985 | 30.3298
|  |  | Potential temperature reduction (see warning below) |  | °C | -2.7402 | -2.4924 | -2.3199 | -2.0333 | -1.7031 | -1.5028 | -1.4463 | -1.7334 | -2.1325 | -2.4724 | -2.8611 | -3.4161 | -4.0401 | -4.4738 | -4.8463 | -5.2462 | -5.6702 | -5.9026 | -5.7915 | -5.5649 | -5.0448 | -4.2125 | -3.493 | -3.0015 | -5.9026
WARNINGS
Actual air temperatures will be lower than these figures suggest as sources of warming aren't considered (the sun, people, etc.)
Water flow will need to be somewhat (20% ?) higher than the 'water evaporated' (to compensate for inefficiencies & minimise mineral deposition in the humidifier)
Note on E35: It's unclear what this value should be, but set it at or below the manufacturer's sensor cut-out
Note on E43: Not used in the wet bulb calculation, BUT the formula used is only valid near sea level (typical value 1013.25 hPa (millibars)
Note on E44: Results verified at https://www.omnicalculator.com/physics/wet-bulb Based on (corrected) formula at https://www.freemathhelp.com/forum/threads/wet-bulb-formula-order-of-operation.131604/ (Stull Formula) The original research paper (https://doi.org/10.1175/JAMC-D-11-0143.1) mentioned in the above says: "An equation is presented for wet-bulb temperature as a function of air temperature and relative humidity at standard sea level pressure. It was found as an empirical fit using gene-expression programming. This equation is valid for relative humidities between 5% and 99% and for air temperatures between −20° and 50°C, except for situations having both low humidity and cold temperature. Over the valid range, errors in wet-bulb temperature range from −1° to +0.65°C, with mean absolute error of less than 0.3°C." Pressure was not used as one of the predictor variables, and hence the resulting regression does not vary with pressure. Also, because the regression equation is only a statistical fit and is not based on physical principles, one cannot assume that it would be valid at other pressures. As an alternative, the reader can use GEP to create new regressions based on Tw, T, and RH% data for any other pressure of interest. Given the quasi-random nature of evolution, it is unlikely that the resulting equations would look like Eq. (1). Namely, both the functional form and the numerical coefficients would likely be considerably different.
Note on E48: August-Roche-Magnus formula Checked output at: https://www.omnicalculator.com/physics/absolute-humidity and https://www.engineeringtoolbox.com/water-vapor-saturation-pressure-d_599.html
Note on E49: Formula: https://www.hatchability.com/Vaisala.pdf page 12 Checked output at: https://www.omnicalculator.com/physics/absolute-humidity
Note on E54: For simplicity it is assumed that temperature & RH follow a linear relationship between the wet & dry bulb temperatures. This may not be the case.
Note on E60: Take value from the MVHR's PassivHaus certificate, if possible. Otherwise deduct 13 from the manufacturer's claimed figure.